## Traffic(all peaks)
Lift traffic design spreadsheet - All Peaks
Enquiries: Dr Gina Barney, Gina Barney Associates, PO Box 7, Sedbergh. LA10 5GE, England. www.liftconsulting.org
Copyright 2003 Gina Barney.Free use (at your risk) provided the whole results page is printed in any report.
DESIGN ID |  |  | 29.06.07
Design Name: |  | Your project name
Design by: |  | Dr Gina Barney
Design Date: |  | 2015-04-24 09:57
INPUT DATA | Value | Comment | Help
Number of floors | 10 | Number of floors (N), range 5-24, above main terminal (MT) | p106
Rated load | 1275 | ISO rated load (kg) | t7.2
Actual car capacity | 13.8 | ISO area/0.21 sq.m. [persons] | t7.2
Number of passengers | 9.4 | Number of passengers (P) [persons] | s5.2
Number of lifts | 5 | Number of lifts (L) [number] | t6.7
Rated speed | 1.6 | Rated speed (v) [m/s] | t5.3
Building population | 800 | Population (POP) expected during peak 5-minutes [persons] | s6.5
Interfloor distance | 3.3 | Average interfloor distance (df) [m] | s7.4
Express jump | 0 | Distance from MT to Express Zone Terminal (EZT) floor - Information only. | e5.22
Express additional time | 0 | Extra time MT to EZT (te-tf(1)) [s] - from dynamics program | e5.22
Single floor flight time | 5 | Time (tf(1)) from instant doors closed until lift level at next landing [s] | t5.3
Door close time | 3 | Time (tc) from instant doors start to close until closed [s] | t5.6
Door open time | 1.8 | Time (to) from instant doors start to open until 800 mm open [s] | t5.6
Advance door opening | 0.5 | Overlap time (tad) of door opening and levelling [s] | t5.6
Start delay | 0.5 | Delay time (td) from instant doors close until motion starts [s] | f5.3 | SCRAP PAD!
Passenger transfer time | 1.2 | Time (tp) one way transfer [s] | s5.9
|  |  |  | tv | T | ts | H | S
RESULTS | Value | Comment | Help | 2.0625 | 9.8 | 7.7375 | 9.4609 | 6.2857
Number of passengers | 9.4 | Given data from above (P) [persons] | s5.2
Highest reversal floor | 9.4611 | Formula (H) [number] WARNING Can differ fromTables 5.1 & 6.8. | e5.12 |  |  | H from k27 | 9.4611 | 10 | s using cc
Number of stops | 6.2857 | Formula (S) [number] | e5.5 | RTT |  |  | 10 | h using cc
Performance time | 9.8 | Time (T) from instant doors start to close until 800 mm open [s] | e5.24 | 117.9601 | rtt as p
Round trip time | 117.9601 | Formula (RTT) [s] | e4.13 | 2574.3625 | rtt as cc | IGNORE | THIS
Interval | 23.592 | Formula (INT) Round trip time/Number of lifts [s] | e4.7 |  | 514.8725 | int as cc
Handling capacity | 119.532 | Formula (UPPHC) [persons/5-minutes] | e4.4 | 14.3443 | awt
Percentage population | 14.9415 | Formula (%POP) Handling capacity/Building population [number] | e4.9
Capacity factor (%) | 68.1159 | Formula (CF) Number of passengers (P)/Actual capacity (AC) [number] | t7.2 | down peak |  | midday
Uppeak average waiting time | 14.3443 | Estimated value passenger average waiting time (AWT) [s] | e6.1 | 75.2402 | rttd | 155.4421 | hcmd
Down peak handling capacity | 187.3998 | Estimated value (DNPHC) [persons/5-minutes] | e13.10
Midday peak handling capacity | 155.4421 | Estimated value (MDDHC) [persons/5-minutes] | e15.2
|  |  |  | 15.048 | intd
COMMENTS: |  |  |  | 187.3998 | hcd
Help refers to the Elevator Traffic Handbook (ISBN 0415274761): p=page; s=section; f=figure; e=equation; t=table.

## Traffic&Basements
Lift traffic design spreadsheet - with Basements
Enquiries: Dr Gina Barney, Gina Barney Associates, PO Box 7, Sedbergh. LA10 5GE, England. www.liftconsulting.org
Copyright 2003 Gina Barney.Free use (at your risk) provided the whole results page is printed in any report.
DESIGN ID |  |  | 29.06.07
Design Name: |  | Your design name
Design by: |  | Your name
Design Date: |  | 2015-04-24 09:57
INPUT DATA | Value | Comment | Help
Number of floors | 24 | Number of floors (N), range 5-24, above main terminal (MT) | p106
Number of basement floors | 3 | Number of floors (M), range 1-5, below main terminal | s8.3.3
Rated load | 800 | ISO rated load [kg] | t7.2
Actual capacity | 12 | ISO area/0.21 sq.m. [persons] | t7.2 | Basement calc
Number of passengers | 9.1 | Number of passengers (P) [persons] | s5.2
% basement passengers | 56 | Percentage of arrivals into basement (persons) | s8.3.3 | P is | 5.096
Number of lifts | 4 | Number of lifts (L) [number] | t6.7 | M is | 3
Rated speed | 1.6 | Rated speed (v) [m/s] | t5.3 | H is for 1 | 1
Building population | 440 | Population (POP) expected during peak 5-minutes [persons] | s6.5 | H is for 2 | 2.9963 | tvm | 1.6875
Interfloor distance | 3.8 | Average interfloor distance (df) [m] | s7.4 | H is for 3 | 2.8696
Basement distance | 2.7 | Average distance between basement floors (m) | s8.3.3
Express jump | 0 | Distance MT to Express Zone Terminal (EZT) floor - Information only. | e5.22 | H is for 4 | 1.8696
Express additional time | 0 | Extra time MT to EZT floor (te-tf(1)) [s] - from dynamics program | e5.22 | H is for 5 | -2.4624
Single floor flight time | 5.1 | Time (tf(1)) from instant doors closed until lift level at next landing [s] | t5.3
Basement flight time | 4.4 | Time (tfB) from instant doors closed until lift level at next landing (s) | s8.3.3
Door close time | 2.6 | Time (tc) from instant doors start to close until closed (s) | t5.6
Door open time | 2 | Time (to) from instant doors start to open until 800 mm open [s] | t5.6 | Hm | 2.8696
Advance door opening | 0.4 | Overlap time (tad) of door opening and levelling [s] | t5.6
Start delay | 0.5 | Delay time (td) from instant doors close until motion starts [s] | f5.3 | SCRAP PAD! |  | tsm | 7.4125 | Sm | 2.62 | 29.1059 | RTTm
Passenger transfer time | 1 | Time (tp) one way transfer [s] | s5.9
|  |  |  | tv | T | ts | H | S
RESULTS | Value | Comment | Help | 2.375 | 9.8 | 7.425 | 22.1205 | 7.7066
Number of passengers | 9.1 | Given data from above (P) [persons] | s5.2
Highest reversal floor | 22.2618 | Formula (H) [number] WARNING Can differ from Tables 5.1 & 6.8. | e5.12 |  |  | H from k27 | 22.2618 | 24 | s using cc
Number of stops | 7.7066 | Formula (S) [number] | e5.5 | RTT |  |  | 24 | h using cc
Performance time | 9.8 | Time (T) from instant doors start to close until 800 mm open [s] | e5.24 | 188.5898 | rtt as p
Round trip time | 217.6957 | Formula (RTT) [s] | e4.13 | 1579.625 | rtt as cc | IGNORE | THIS
Interval | 54.4239 | Formula (INT) Round trip time/Number of lifts [s] | e4.7 |  | 394.9062 | int as cc
Handling capacity | 50.1618 | Formula (UPPHC) [persons/5-minutes] | e4.4 | 41.037 | awt
Percentage population | 11.4004 | Formula (%POP) Handling capacity/Building population [number] | e4.9
Capacity factor (%) | 75.8333 | Formula (CF) Number of passengers (P)/Actual capacity (AC) [number] | t7.2 | down peak
Average waiting time | 41.037 | Estimated value passenger average waiting time (AWT) [s] | e6.1 | 111.2357 | rttd
Down peak handling capacity | 98.1699 | Estimated value (DNPHC) [persons/5-minutes] | e13.10
|  |  |  | 27.8089 | intd
COMMENTS: |  |  |  | 98.1699 | hcd
Help refers to the Elevator Traffic Handbook (ISBN 0415274761): p=page; s=section; f=figure; e=equation; t=table.

## DoubleDeck
Lift traffic design spreadsheet - Double Deck
Enquiries: Dr Gina Barney, Gina Barney Associates, PO Box 7, Sedbergh. LA10 5GE, England. www.liftconsulting.org
Copyright 2003 Gina Barney.Free use (at your risk) provided the whole results page is printed in any report.
DESIGN ID |  |  | 19.1.7
Design Name: |  | h
Design by: |  | Dr Gina Barney
Design Date: |  | 2015-04-24 09:57
INPUT DATA | Value | Comment | Help
Number of floors served by one deck | 8 | Number of floors (N), range 5-24, above main terminal (MT) | p106
Rated load | 1600 | ISO rated load (kg) | t7.2
Actual capacity | 16.9 | ISO area/0.21 sq.m. [persons] | t7.2
Number of passengers | 13.5 | Number of passengers (P) [persons] | s5.2
Number of lifts | 6 | Number of lifts (L) [number] | t6.7
Rated speed | 4 | Rated speed (v) [m/s] | t5.3
Total building population | 2363 | Population (POP) expected during peak 5-minutes [persons] | s6.5
Double interfloor distance | 8 | Average interfloor distance (df) [m] | s7.4
Express jump | 0 | Distance from MT to Express Zone Terminal (EZT) floor - Information only. | e5.22
Express additional time | 0 | Extra time MT to EZT (te-tf(1)) [s] - from dynamics program | e5.22
Double floor flight time | 6.36 | Time (tf(1)) from instant doors closed until lift level at next landing [s] | t5.3
Door close time | 2.8 | Time (tc) from instant doors start to close until closed [s] | t5.6
Door open time | 2 | Time (to) from instant doors start to open until 800 mm open [s] | t5.6
Advance door opening | 0.5 | Overlap time (tad) of door opening and levelling [s] | t5.6 |  | h | i | j | k | l
Start delay | 0.4 | Delay time (td) from instant doors close until motion starts [s] | f5.3 | SCRAP PAD!
Passenger transfer time | 1 | Time (tp) one way transfer [s] | s5.9
|  |  |  | tv | T | ts | H | S
RESULTS | Value | Comment | Help | 2 | 11.06 | 9.06 | 7.8127 | 6.6811 |  | 29
Number of passengers | 13.5 | Given data from above (P) [persons] | s5.2 | [6 empty] | 30
Highest reversal floor | 7.8127 | Formula (H) [number] WARNING Can differ fromTables 5.1 & 6.8. | e5.12 |  |  | H from k27 | 7.8127 | 8 | s using cc | 31
Number of stops | 6.6811 | Formula (S) [number] | e5.5 | RTT |  |  | 8 | h using cc
Performance time | 11.06 | Time (T) from instant doors start to close until 800 mm open [s] | e5.24 | 140.0466 | rtt as p
Round trip time | 140.0466 | Formula (RTT) [s] | e4.13 | 2673.54 | rtt as cc | IGNORE | THIS
Interval | 23.3411 | Formula (INT) Round trip time/Number of lifts [s] | e4.7 |  | 445.59 | int as cc
Handling capacity | 347.0273 | Formula (UPPHC) [persons/5-minutes] | e4.4 | 19.7477 | awt
Percentage population | 14.6859 | Formula (%POP) Handling capacity/Building population [number] | e4.9
Capacity factor (%) | 79.8817 | Formula (CF) Number of passengers (P)/Actual capacity (AC) [number] | t7.2 | down peak
Average waiting time | 19.7477 | Estimated value passenger average waiting time (AWT) [s] | e6.1 | 82.3256 | rttd
Down peak handling capacity | 590.3391 | Estimated value (DNPHC) [persons/5-minutes] | e13.10
|  |  |  | 13.7209 | intd
COMMENTS: |  |  |  | 590.3391 | hcd
Help refers to the Elevator Traffic Handbook (ISBN 0415274761): p=page; s=section; f=figure; e=equation; t=table.

## Traffic(hall call)
Lift traffic design spreadsheet - All Peaks
Enquiries: Dr Gina Barney, Gina Barney Associates, PO Box 7, Sedbergh. LA10 5GE, England. www.liftconsulting.org
Copyright 2003 Gina Barney.Free use (at your risk) provided the whole results page is printed in any report.
DESIGN ID |  |  |  | 29.06.07
Design Name: |  |  | Your project name
Design by: |  |  | Dr Gina Barney
Design Date: |  |  | 2015-04-24 09:57
INPUT DATA | Value |  | Comment | Help
Number of floors | 19 |  | Number of floors (N), range 5-24, above main terminal (MT) | p106
Rated load | 1800 |  | ISO rated load (kg) | t7.2
Actual capacity | 24 |  | ISO area/0.21 sq.m. [persons] | t7.2
Number of passengers | 19.2 |  | Number of passengers (P) [persons] | s5.2
Number of lifts | 8 |  | Number of lifts (L) [number] | t6.7
Rated speed | 2.5 |  | Rated speed (v) [m/s] | t5.3
Building population | 1900 |  | Population (POP) expected during peak 5-minutes [persons] | s6.5
Interfloor distance | 4.25 |  | Average interfloor distance (df) [m] | s7.4
Express jump | 0 |  | Distance from MT to Express Zone Terminal (EZT) floor - Information only. | e5.22
Express additional time | 0 |  | Extra time MT to EZT (te-tf(1)) [s] - from dynamics program | e5.22
Single floor flight time | 5.4 |  | Time (tf(1)) from instant doors closed until lift level at next landing [s] | t5.3
Door close time | 2 |  | Time (tc) from instant doors start to close until closed [s] | t5.6
Door open time | 2 |  | Time (to) from instant doors start to open until 800 mm open [s] | t5.6
Advance door opening | 0.7 |  | Overlap time (tad) of door opening and levelling [s] | t5.6
Start delay | 0.6 |  | Delay time (td) from instant doors close until motion starts [s] | f5.3 | SCRAP PAD!
Passenger transfer time | 1 |  | Time (tp) one way transfer [s] | s5.9 | [6 empty] | Hall call
Look ahead | 8 |  | Look ahead (k)
[5 empty] | tv | T | ts | H | S |  | S hall
RESULTS | Value |  | Comment | Help | 1.7 | 9.3 | 7.6 | 18.4764 | 12.2715 |  | 2.3744
Number of passengers | 19.2 |  | Given data from above (P) [persons] | s5.2 | [6 empty] | H hall
Highest reversal floor | 18.4764 |  | Formula (H) [number] WARNING Can differ fromTables 5.1 & 6.8. | e5.12 |  |  | H from k27 | 18.4773 | 19 | s using cc | 14.6177
Number of stops | 12.2715 |  | Formula (S) [number] | e5.5 | RTT |  |  | 19 | h using cc |  | RTT hall
Performance time | 9.3 |  | Time (T) from instant doors start to close until 800 mm open [s] | e5.24 | 202.0863 | rtt as p |  |  |  |  | 113.7459
Round trip time | 202.0863 |  | Formula (RTT) [s] | e4.13 | 3096.6 | rtt as cc | IGNORE | THIS |  |  | INT hall
Interval | 25.2608 |  | Formula (INT) Round trip time/Number of lifts [s] | e4.7 |  | 387.075 | int as cc |  |  |  | 14.2182
Handling capacity | 228.0214 |  | Formula (UPPHC) [persons/5-minutes] | e4.4 | 24.3438 | awt |  |  |  |  | HC hall
Percentage population | 12.0011 |  | Formula (%POP) Handling capacity/Building population [number] | e4.9 | [6 empty] | 405.1136
Capacity factor (%) | 80 |  | Formula (CF) Number of passengers (P)/Actual capacity (AC) [number] | t7.2 | down peak |  | midday
Uppeak average waiting time | 24.3438 |  | Estimated value passenger average waiting time (AWT) [s] | e6.1 | 124.9318 | rttd | 282.572 | hcmd
Uppeak journey time | 105.0498 | [9 empty] | AJT hall
Down peak handling capacity | 368.8412 |  | Estimated value (DNPHC) [persons/5-minutes] | e13.10 |  |  | AJT |  |  |  | 105.1025
Midday peak handling capacity | 282.572 |  | Estimated value (MDDHC) [persons/5-minutes] | e15.2 |  |  | 105.0498
Hall call number of stops | 2.3744
Hall call highest reversal floor | 14.6177
Hall call interval | 14.2182
Hall call handling capacity | 405.1136 | 1.7766
HCA uppeak AWT | 56.8729
HCA journey time | 105.1025
[5 empty] | 15.6165 | intd
COMMENTS: |  |  |  |  | 368.8412 | hcd
Help refers to the Elevator Traffic Handbook (ISBN 0415274761): p=page; s=section; f=figure; e=equation; t=table.

## Lift dynamics
Lift dynamics calculation spreadsheet by Dr Gina Barney. Free (at your risk) use provided source acknowledged. www.liftconsulting.org
180107
Project Name | Enter your project name here
2015-04-24 09:57 | Entries
Rated speed (m/s) | 1.6
Rated acceleration (m/s^2) | 0.7 | 0 | 0
Jerk (m/s^3) | 1.1 | 2.5126 | 1.3134
Trip distance (m) | 3.3 | 2.5126 | 1.3134
Flight time for trip distance (s) | 5.0252 | 5.0252 | 0
Maximum speed reached during trip (m/s) | 1.3134
Distance to reach maximum speed (m) | 2.3377
Minimum trip distance to reach maximum speed (m) | 4.6753
Calculation details
Possible speed for trip distance (m/s) | 1.3134 |  |  | #REF!
Trip time if rated speed is reached during trip (s) | 4.9846 |  |  | 0
Trip time if rated speed not reached during trip (s) | 5.0252
Distance to v if amax not reached | 1.9319
Acceleration at max speed | 1.3266
Time to max speed | 2.4121
Trip time | 4.4719
Flight time for trip distance | 5.0252
Distance to reach rated speed | 2.3377